|  | Information for owners and managers of hotels and other accommodation sites: minimising the risk: Nearly 700 cases of travel associated legionnaires' disease in European residents were reported to the European surveillance scheme in 2002. The risk from legionnaires' disease can be reduced by careful attention to a number of simple measures. This page contains summary information for site owners and hotel managers and also provides links to other relevant resources. What is legionnaires' disease? An uncommon form of pneumonia (lung infection) from which approximately 13% of those that become ill will die. It is caused by legionella bacteria. These bacteria can also cause less serious illness. The infected person usually begins to feel unwell 3-6 days after they have caught the infection, although it may take longer. Symptoms The illness usually starts with a fever, chills, headache and muscle pain. This is followed by a dry cough and breathing difficulties that may progress to severe pneumonia. About 30% of those infected will also have diarrhoea or vomiting and about 50% become confused or delirious. Accurate diagnosis requires specific laboratory tests that often are not done until the guests have returned home. How is legionnaires' disease caught? By breathing in air containing the legionella bacteria in invisible water droplets known as an aerosol. Aerosols can be formed whenever fine droplets are generated from contaminated water. In hotels with no effective legionella control programme this may be from running a tap or shower, flushing a toilet, or from bubbles rising through water in a spa pool. The bacteria, which also live naturally in the environment can live and multiply in water at temperatures of 20°C to 45°C and high numbers occur in inadequately maintained man-made water systems. Where are the risk areas in an hotel? Wherever water droplets can be created there is a risk of infection e.g.: Showers and taps. Spa baths and whirlpool baths. Turkish baths and saunas. Cooling towers and evaporative condensers used for air conditioning, even if situated on the roof or in the grounds. Ornamental fountains, particularly indoors. Humidified food displays. Where can legionella multiply? Hot and cold water tanks / cisterns. Warm water between 20°C and 45°C. Pipes with little or no water flow (this includes unoccupied rooms). Slime (biofilm) and dirt on pipe and tank surfaces. Rubber and natural fibres in washers and seals. Water heaters and hot water storage tanks. Scale in pipes, showers and taps.. These situations and conditions encourage the growth of legionella bacteria and increase the risk of infection to hotel guests and staff. Reducing the risk - the 14 point checklist The risk of legionnaires' disease can be minimised. Any hotel that does not have an active programme to control the growth of legionella bacteria is negligent in ensuring the safety of their guests. This programme should include the following: 1.; Have one named person responsible for legionella control.. 2.; Ensure the named person is trained in control of legionella and other staff are trained to be aware of the importance of their role in controlling legionella. 3.; Keep hot water hot and circulating at all times: 50 oC - 60oC (too hot to put hands into for more than a few seconds). 4.; Keep cold water cold at all times. It should be maintained at temperatures below 25oC. 5.; Run all taps and showers in guest rooms for several minutes at least once a week if they are unoccupied and always prior to occupation.. 6.; Keep shower heads and taps clean and free from scale. 7.; Clean and disinfect cooling towers and associated pipes used in air conditioning systems regularly - at least twice a year. 8.; Clean and disinfect water heaters (calorifiers) once a year. 9.; Disinfect the hot water system with high level (50mg/l) chlorine for 2-4 hours after work on water heaters and before the beginning of every season. 10.; Clean and disinfect all water filters regularly - every one to three months. 11.; Inspect water storage tanks, cooling towers and visible pipe work monthly. Ensure that all coverings are intact and firmly in place. 12.; Inspect the inside of cold water tanks at least once a year and disinfect with 50mg/l chlorine and clean if containing a deposit or otherwise dirty. 13.; Ensure that system modifications or new installations do not create pipework with intermittent or no water flow. 14.; If there is a spa pool (also known as whirlpool spas, "Jacuzzis", spa baths) ensure that: It is continuously treated with 2-3mg/l chlorine or bromine and the levels are monitored at least three times a day. At least half of the water is replaced each day. Sand filters are backwashed daily. The whole system is cleaned and disinfected once a week. Daily records of all water treatment readings such as temperature and chlorine concentrations are kept and ensure they are checked regularly by the manager... Further advice about specific controls should be sought from experts in this field who can carry out a full risk assessment of the hotel site. Your local public health authorities may be able to recommend a good source of advice. Legionella testing Testing for legionella is a useful tool but only on condition that it is carried out by trained personnel. Water samples should be examined by laboratories accredited for testing water for legionella bacteria (e.g. by UKAS or equivalent national bodies elsewhere). A negative test result does not necessarily mean that the hotel is clear of legionella or that there is no risk. Accreditation of water treatment companies The co-ordinating centre in London has been asked by some water treatment companies if they can obtain EWGLI accreditation for carrying out legionella risk assessments at hotels. EWGLI does not have the authority or legal status to give such accreditation to any company. Further information Further information on managing risk can be obtained from the European Guidelines for Control and Prevention of Travel Associated Legionnaires’ Disease.. |  |
| --- | --- | --- |
|  | Site Updates ¦ Public Information ¦ Data ¦ Search ¦ Links ¦ Contact Us ¦ Subscribe ¦ Home.. All material in this site © Copyright The European Working Group for Legionella Infections 1999 - 2005. |  |